SCHEDULE 15

STANDARD TECHNICAL CONDITIONS, HOSTING CAPACITY INFORMATION, AND SHORT-FORM SYSTEM IMPACT STUDY CONFIRMATION FOR ELIGIBLE INTERCONNECTED SOLAR PV AND BATTERY MINI-GRIDS

To form part of the Mini-Grid Regulations, 2026

1. Purpose and Application

1.1 This Schedule prescribes the standard technical conditions applicable to an eligible interconnected solar photovoltaic and battery mini-grid seeking to rely on the simplified interconnection pathway under section 9 of the Mini Grid Regulations 2026.

1.2 This Schedule applies only to interconnected mini-grids based on solar photovoltaic generation and battery energy storage systems, including a project transitioning from isolated to interconnected status where the project seeks to rely on the Short-Form SIS pathway.

1.3 This Schedule does not displace the need for compliance with applicable health and safety requirements, environmental screening, metering, inspection, commissioning, energisation approval, or any other applicable requirement under the Mini Grid Regulations 2026 or any relevant code.

1.4 Nothing in this Schedule creates deemed energisation approval, deemed safety clearance, or waiver of any applicable technical requirement.

2. Interpretation

2.1 In this Schedule, unless the context otherwise requires—

“Battery energy storage system” or “BESS” means a battery-based electricity storage system including the battery cells, battery management system, inverter or converter, and associated protection, control, and isolation equipment;

“Eligible project” means a proposed interconnected solar photovoltaic and battery mini-grid that satisfies the qualifying conditions in this Schedule and may therefore rely on a Short-Form SIS Confirmation;

“Hosting Capacity Information” or “HCI” has the meaning assigned to it in the Mini Grid Regulations 2026;

“Managed export project” means an eligible project permitted to export electricity at the PCC subject to dynamic or time-varying limits, communications, or control instructions approved by the Commission;

“Limited export project” means an eligible project permitted to export electricity at the PCC up to a fixed approved export limit;

“non-export project” means an eligible project that may import electricity from the Distribution Licensee where permitted but is not authorised to export electricity into the Distribution Licensee’s network during normal operation except to the extent expressly permitted for testing, meter tolerance, or transient events;

“Short-Form System Impact Study Confirmation” means the standard written confirmation, in the form prescribed in this Schedule or otherwise approved by the Commission, confirming that an eligible project satisfies the simplified interconnection pathway based on applicable Hosting Capacity Information, the project's single-line diagram, and conformity with the standard technical conditions in this Schedule.

3. General Principles

3.1 Proportionality: the level of technical review shall reflect the size, technology, export behaviour, and system risk of the project.

3.2 Non-discrimination: equivalent projects on equivalent feeders should be subject to equivalent technical treatment.

3.3 Feeder transparency:  Hosting Capacity Information should be sufficiently informative to permit developers to assess likely eligibility before full application.

3.4 Safety first: no simplified pathway shall compromise safety, protection coordination, or the integrity of the affected network.

3.5 PCC discipline: the PCC is the technical and commercial boundary for interconnection review, metering, and settlement.

3.6 Nigerian market realism: this Schedule recognises stressed feeders, variable data quality, routine outages, and the need for simple but robust connection standards in Nigeria.

4. Eligibility for the Short-Form System Impact Study Pathway

4.1 A project may rely on the simplified pathway only where all the conditions in this paragraph are satisfied.

4.2 The project shall be inverter-based and shall not rely on synchronous generation operating in parallel with the Distribution Licensee’s network under the simplified pathway unless specifically authorised by the Commission.

4.3 The project shall have one clearly identified PCC and shall connect through a radial feeder arrangement.

4.4 The applicable  Hosting Capacity Information shall show sufficient available capacity for the proposed import profile and, where relevant, export profile at the PCC.

4.5 The project shall conform to the applicable operating mode and standard technical conditions prescribed in this Schedule.

4.6 The project shall not require major network reinforcement, meshed-network studies, or complex protection redesign beyond the standard protection package and minor connection works.

4.7 The project shall provide a single-line diagram, equipment schedule, protection schedule, metering arrangement, and site layout sufficient to confirm conformance with this Schedule.

4.8 The Commission or the Distribution Licensee may require a full SIS notwithstanding apparent eligibility where feeder conditions, power quality, protection, reverse power flow, or operational coordination risks are not adequately addressed by the simplified pathway.

5. Operating Modes for Eligible Projects

5.1 An eligible project shall operate in one, and only one, of the following operating modes:

(a) Non-Export Interconnected Project;

(b) Limited Export Interconnected Project;

(c) Managed Export Interconnected Project.

5.2 A non-export project may use solar photovoltaic generation and battery storage to serve its customers and may import electricity from the Distribution Licensee where permitted, but it shall not export electricity to the Distribution Licensee’s network during normal operation.

5.3 A limited export project may supply its own customers and may export electricity to the Distribution Licensee’s network only up to the fixed approved export limit stated in the Hosting Capacity Information, permit, Tripartite Agreement, or Commission direction.

5.4 A managed export project may export electricity to the Distribution Licensee’s network subject to dynamic or time-varying limits, communications requirements, or operating instructions approved for the relevant feeder.

5.5 The approved operating mode of the project shall be stated in the permit, the Short-Form SIS Confirmation, and the Technical and Commercial Annex in Schedule 10.

6. General Technical Conditions Applicable to All Eligible Projects

6.1 The technical, ownership, protection, metering, and commercial boundary at the PCC shall be clearly identified and reflected in the single-line diagram and Tripartite Agreement.

6.2 The simplified pathway assumes a radial feeder arrangement. Projects involving looped or meshed network effects shall be referred for a fuller study.

6.3 Inverter-based resources shall use equipment listed or certified to recognised standards acceptable to the Commission or the competent inspection authority and shall be capable of anti-islanding and such voltage, frequency, reactive power, ramp-rate, and communications functions as may be required for the relevant operating mode.

6.4 The project shall be designed not to cause unacceptable harmonics, flicker, voltage unbalance, or rapid voltage change at the PCC and shall comply with applicable limits in the Distribution Code and manufacturer-recommended operating ranges.

6.5 The project shall include the minimum protection package in Appendix 1 and any project-specific settings directed by the Distribution Licensee or approved by the Commission.

6.6 Import and export metering at the PCC shall comply with the Metering Code, the interconnection agreement, and any applicable commercial methodology.

6.7 The operator shall nominate control and maintenance contacts and comply with outage-notification and emergency-isolation arrangements agreed under the Tripartite Agreement.

7. Minimum Protection, Metering, and Communications Requirements

7.1 At a minimum, the interconnection shall provide over-voltage, under-voltage, over-frequency, under-frequency, anti-islanding, overcurrent or earth-fault protection, and an isolating device capable of safe disconnection at or near the PCC.

7.2 Where export is permitted, the project shall include control logic and settings sufficient to respect approved export limits, prevent unstable reverse power flow, and coordinate with the feeder protection philosophy.

7.3 Protection settings shall be submitted in the Short-Form PCC Confirmation and shall be subject to validation by the Distribution Licensee.

7.4 The Distribution Licensee shall provide PCC metering adequate for import measurement and, where applicable, export measurement.

7.5 Export-enabled projects shall provide interval data sufficient for settlement and operational review.

7.6 The Mini-Grid operator may install a check meter, but the primary meter for settlement shall be the approved PCC meter unless otherwise approved by the Commission.

7.7 Non-export projects shall require only basic contact and alarm arrangements unless the Commission directs otherwise.

7.8 Limited export projects shall require remote visibility of PCC meter data, breaker status, and plant availability alarms.

7.9 Managed export projects shall require enhanced communications, including remote setting capability, event logs, and telemetry reasonably necessary for safe operation.

8. Battery-Specific Requirements

8.1 The battery system shall include a battery management system, emergency isolation arrangement, manufacturer-approved operating limits, and fault or alarm indication.

8.2 Battery rooms or enclosures shall comply with applicable health and safety, ventilation, fire, earthing, labelling, and emergency-response requirements under the Mini Grid Regulations 2026 and any applicable inspection requirement.

8.3 The project shall submit the battery datasheet, operating envelope, short-circuit contribution statement where relevant, and control philosophy for charge and discharge relative to import and export behaviour at the PCC.

8.4 For export-enabled projects, the battery dispatch logic shall be described clearly enough to enable the Distribution Licensee and the Commission to understand whether the battery is intended for backup, energy shifting, peak support, export shaping, or multiple functions.

9. Hosting Capacity Information and Minimum Data Requirements

9.1 The Hosting Capacity Information shall be feeder-level information published by the Distribution Licensee in the form approved by the Commission.

9.2 In addition to the minimum fields required by the Mini Grid Regulations 2026, the Distribution Licensee should, where available, publish the date of issue, date of last update, feeder status, indicative import capacity, indicative export headroom, major known deficiencies, and any standard conditions or exclusions relevant to interconnection on that feeder.

9.3 The Hosting Capacity Information remains indicative only and does not, by itself, create a right to connect. However, where such information is published and remains current, it shall be the primary basis for determining whether the simplified pathway is available.

10. Short-Form System Impact Study Confirmation

10.1 The Short-Form System Impact Study Confirmation is a structured engineering and regulatory declaration that the proposed project conforms to the applicable operating mode and that feeder-level Hosting Capacity Information supports the requested interconnection.

10.2 The Short-Form Hosting Capacity Information Confirmation shall be signed by a competent person designated by the mini-grid developer and agreeable to the Distribution Licensee, and accompanied by the documents listed in Appendix 2.

10.3 The Distribution Licensee shall review the Short-Form System Impact Study Confirmation only to the extent necessary to determine whether the project conforms to this Schedule, whether the Hosting Capacity Information supports the interconnection, and whether any limited project-specific condition or rectification is required.

10.4 The Short-Form System Impact Study Confirmation shall contain, at minimum, the project identity, location, feeder and PCC reference, technology description, installed capacities, single-line diagram, site layout, protection schedule, metering arrangement, declared import and export mode, evidence that the  Hosting Capacity Information remains current for the feeder, and a declaration of compliance with this Schedule and the Distribution Code.

11. Cases Requiring a Full System Impact Study

11.1 A full System Impact Study shall be required where any of the following applies:

(a) the project has multiple PCC or a materially complex feeder arrangement;

(b) the project proposes parallel operation of synchronous generation with the Distribution Licensee’s network;

(c) major reinforcement, network reconfiguration, or protection redesign appears necessary;

(d) the Hosting Capacity Information is unavailable, stale, materially incomplete, or contradicted by known feeder conditions;

(e) the project seeks export beyond the feeder’s indicated capability or seeks unrestricted export on a stressed feeder;

(f) the project raises unresolved concerns on voltage profile, short-circuit contribution, reverse power flow, harmonics, flicker, or protection coordination;

(g) the project falls outside the capacity band or technical envelope of the standard technical conditions prescribed in Schedule 15 to these Regulations;

(h) the Commission or the Distribution Licensee identifies any site-specific technical risk that cannot reasonably be addressed through a short-form review.

12. Review Outcome and Conditions

12.1 On review of a Short-Form SIS Confirmation, the Distribution Licensee may confirm that the proposed interconnection is acceptable as submitted, acceptable subject to stated conditions, or not acceptable under the simplified pathway.

12.2 Any condition imposed shall be specific, proportionate, and reasonably necessary for safety, metering integrity, operational coordination, or power quality.

12.3 Refusal of the simplified pathway shall be stated in writing with sufficient technical reasons to enable the developer to understand whether a full SIS, limited rectification, or a different feeder or operating mode is required.

13. Relationship with Schedule 10 and Project Documents

13.1 Where a project relies on section 9 of the Mini Grid Regulations 2026, the Mandatory Technical and Commercial Annex in Schedule 10 shall identify the approved operating mode and any approved deviation from the standard technical conditions prescribed in Schedule 15 to these Regulations.

13.2 The Tripartite Agreement, Interconnection Agreement, and permit shall remain the authoritative project-specific instruments for operating conditions, protection settings, outage coordination, metering, and communications obligations.

13.3 Nothing in this Schedule prevents the Commission from imposing additional project-specific conditions in the permit or approved contracts where feeder conditions or system security so require.

14. Compliance, Inspection, and Review

14.1 A project approved through the simplified pathway shall be subject to inspection, testing, and energisation approval requirements applicable under the Mini Grid Regulations 2026, any applicable inspection requirement, and any direction of the Commission.

14.2 If a project is found, before or after energisation, not to conform materially to the Approved Operating Mode or standard technical conditions relied upon, the Commission may direct corrective action, require a fuller study, suspend export, or take such other regulatory action as it considers appropriate.

14.3 The Commission may revise the prescribed forms, templates, and appendices from time to time, having regard to technological development, field experience, the Distribution Code, and the needs of the Nigerian electricity market.

APPENDIX 1

Minimum Standard Conditions Matrix

| Item | Non-Export Project | Limited Export Project | Managed Export Project | Mandatory | Notes |
| --- | --- | --- | --- | --- | --- |
| Single PCC | Yes | Yes | Yes | Yes | Projects with multiple PCCs fall outside the simplified pathway. |
| Radial feeder only | Yes | Yes | Yes | Yes | Looped or meshed network effects require case-specific review. |
| Solar PV + battery | Yes | Yes | Yes | Yes | Other technologies may be added by later Commission order. |
| Synchronous generation in parallel with DisCo network | No | No | Case-specific | Yes | If proposed, a full study is ordinarily required. |
| Routine export | No | Limited only | Managed only | By operating mode | Export mode must match approved limits and control settings. |
| Standard protection package | Yes | Yes | Yes | Yes | See Appendix 2 checklist. |
| PCC import meter | Yes | Yes | Yes | Yes | Primary meter for settlement unless otherwise approved. |
| PCC export meter | Not required | Required | Required | If export enabled | May be combined or separate depending on approved metering solution. |
| Remote visibility | Optional | Required | Required | By operating mode | At minimum for export-enabled projects. |
| Major reinforcement | Not required | Not required | Case-specific | No | If required, the full study path is ordinarily triggered. |

APPENDIX 2

Short-Form System Impact Study Confirmation Template

This template shall be completed by the developer and signed by a competent technical signatory. The Distribution Licensee shall complete Section H following review.

A. Project Identification and Application Details

| Field | Information to be completed |
| --- | --- |
| Project name / reference |  |
| Mini-grid developer / permit applicant |  |
| Project location (State / LGA / Community) |  |
| Project type | Solar PV only / Solar PV + BESS / BESS-supported IMG / Other |
| Installed PV capacity (kWp / MWp) |  |
| Installed battery capacity (kWh / MWh) and inverter rating |  |
| Requested date of interconnection/energisation |  |
| Name, title, and contact details of the responsible technical signatory |  |

B. Feeder, PCC, and Interconnection Data

| Field | Information to be completed |
| --- | --- |
| Distribution Licensee |  |
| Supplying substation |  |
| Feeder name/feeder code |  |
| Voltage level at PCC |  |
| PCC reference / pole / RMU / transformer / location marker |  |
| Radial feeder confirmation | Yes / No |
| Existing Hosting Capacity Information publication reference and date |  |
| Requested import capacity at PCC (KW/ MW) |  |
| Requested export capacity at PCC (kW/ MW), if any |  |

C. Approved Operating Mode

| Field | Information to be completed |
| --- | --- |
| Selected operating mode | Non-Export / Limited Export / Managed Export |
| Reason the selected operating mode applies |  |
| Any project-specific deviation requested | None / Yes — describe |
| Does the project require a full SIS instead of the short-form route? | No / Yes — explain |

D. Generating Plant and Battery Characteristics

| Field | Information to be completed |
| --- | --- |
| PV module manufacturer / model |  |
| Total inverter AC rating |  |
| Battery manufacturer / model |  |
| Battery usable energy capacity |  |
| Battery discharge duration at rated output |  |
| Standby generator behind mini-grid | None / Yes — describe |
| Normal operating mode | Import only / Import + no export / Import + limited export / Managed export |

E. Protection, Metering, and Communications

| Field | Information to be completed |
| --- | --- |
| Anti-islanding provided | Yes / No |
| Voltage and frequency protection provided | Yes / No |
| Export limiting control provided | Not applicable / Yes |
| PCC metering arrangement |  |
| Check meter proposed | No / Yes |
| Communications/telemetry arrangement |  |
| Operating contact for outage coordination |  |

F. Hosting Capacity Information Basis and Key Assumptions

| Field | Information to be completed |
| --- | --- |
| Does published Hosting Capacity Information show sufficient available capacity? | Yes / No |
| Known feeder limitations identified in Hosting Capacity Information |  |
| Assumed import limit used in review |  |
| Assumed export limit used in review |  |
| Any reinforcement or protection modification required | No / Yes — describe |
| Basis for concluding project fits short-form pathway |  |

G. Developer Technical Declaration

| Declaration item | Confirmation |
| --- | --- |
| The project information in this form is accurate and complete. | Confirmed / Not confirmed |
| The project conforms to the approved operating mode and the applicable standard technical conditions in Schedule 15. | Confirmed / Not confirmed |
| The submitted single-line diagram, layout, equipment schedule, and protection schedule are current and consistent with this form. | Confirmed / Not confirmed |
| The project will comply with the Distribution Code, Metering Code, applicable safety requirements, and Commission directions. | Confirmed / Not confirmed |
| Name/signature/date of competent technical signatory |  |

H. Distribution Licensee Review Outcome

| Field | Distribution Licensee entry |
| --- | --- |
| Short-form SIS status | Accepted / Accepted with conditions / Rejected |
| If accepted with conditions, state the conditions |  |
| If rejected, state specific technical reasons |  |
| Additional information required, if any |  |
| Reviewer name, title, signature, and date |  |

Short-Form System Impact Study Confirmation – Minimum Submission Checklist

| Submission Item | Required for all operating modes? | Notes |
| --- | --- | --- |
| Application cover letter | All | Identify feeder, PCC, and requested review path. |
| Single-line diagram | All | Shall clearly show PCC, metering, protection, PV, battery, controller, and any backup source. |
| Site layout | All | Include switchgear, battery enclosure, earthing, access, and emergency isolation points. |
| Equipment schedule and datasheets | All | PV modules, inverters, battery, protection devices, breakers, meters, plant controller. |
| Protection schedule and proposed settings | All | Provide functions and setpoints proposed for validation. |
| Battery control philosophy | All | Explain backup, charge/discharge, import/export, and any islanded operation logic. |
| Hosting Capacity Information reference | All | Identify Hosting Capacity Information issue date and feeder record relied upon. |
| Export limit declaration | Export-enabled only | State no export, fixed export limit, or managed export control. |
| Communications description | Export-enabled only | Describe meter visibility, telemetry, alarms, remote setpoints where applicable. |
| Competent person declaration | All | Signed by responsible engineer or competent technical representative. |

APPENDIX 3

Minimum Hosting Capacity Information Template

This template shall be published by each Distribution Licensee in the form approved by the Commission and updated at the frequency directed by the Commission.

A. Publication Metadata

| Field | Information to be completed by Distribution Licensee |
| --- | --- |
| Distribution Licensee |  |
| Publication reference/version number |  |
| Date of publication |  |
| Period of validity |  |
| Responsible office/contact for clarification |  |

B. Feeder-Level Hosting Capacity Information Table

| Feeder Name / Code | Supplying Substation | Voltage Level | Network Type / Radial Status | Indicative Import Capacity at PCC | Indicative Export Capacity at PCC | Applicable Operating Mode Supported | Known Operational / Protection Limits | Standard Interconnection Conditions | Date Last Updated |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

C. Minimum Field Notes and Assumptions

| Field / Topic | Required description |
| --- | --- |
| Indicative Import Capacity at PCC | State the approximate maximum additional import capability that may be accommodated at the referenced feeder location under normal planning assumptions. |
| Indicative Export Capacity at PCC | State the approximate maximum export capability that may be accommodated without triggering a full SIS, subject to project conformance with the applicable operating mode and the standard technical conditions prescribed in Schedule 15 to these Regulations. |
| Applicable Operating Mode Supported | State whether the feeder is suitable for non-export only, limited export, or managed export, and identify any capacity band, operating restriction, communication requirement or control condition attached to that classification. |
| Known Operational / Protection Limits | State any known reverse power flow limitations, protection constraints, voltage concerns, reliability concerns, or operating restrictions relevant to interconnection. |
| Standard Interconnection Conditions | State any standard requirements for metering, telemetry, breaker type, export limiter, PCC arrangement, outage coordination, or testing that ordinarily apply on the feeder. |
| Validity of Hosting Capacity Information | State the period for which the Hosting Capacity Information is considered current, after which the Distribution Licensee may require refreshed confirmation. |
| Basis of Values | State whether the published values are based on studies, feeder data, planning assumptions, historical loading, engineering estimates, or other Commission-accepted basis. |
| Important Caveat | State that the Hosting Capacity Information is indicative and does not of itself create a right to connect or energise, but may support the simplified pathway where the project conforms to the applicable operating mode and technical conditions. |
| Update Frequency | State the minimum frequency of update and the trigger for unscheduled revision where feeder conditions materially change. |

D. Use of the Template

The Distribution Licensee shall publish the feeder-level table in an editable and searchable format approved by the Commission. Each row shall correspond to a distinct feeder or clearly defined feeder segment relevant to mini-grid interconnection planning.

Where the Distribution Licensee does not have sufficient feeder-level data to populate a field precisely, the field shall be completed using the best available engineering estimate together with a note on the basis used and any material limitation of that estimate.

Minimum Hosting Capacity Information Template – Field Summary

| Field | Minimum / Optional | Guidance |
| --- | --- | --- |
| Feeder name/code | Minimum | Use the official feeder identifier used by the Distribution Licensee. |
| Voltage level | Minimum | Specify LV, 11 kV, 33 kV, or other approved class. |
| Supplying injection substation | Minimum | Where applicable. |
| Date issued/updated | Minimum | State the date of last update and validity horizon. |
| Indicative import capacity at PCC | Minimum | May be stated as feeder-level indicative capacity subject to site confirmation. |
| Indicative export headroom | Optional but recommended | Especially important where the simplified export pathway is contemplated. |
| Known operational limitations | Minimum | For example, protection deficiency, chronic low voltage, overload constraints, or outage constraints. |
| Standard interconnection conditions | Minimum | Any standard restrictions, settings, export caps, telemetry expectations. |
| Existing embedded generation / IMG | Optional but recommended | Useful for cumulative penetration assessment. |