SCHEDULE 7

MINIMUM TECHNICAL REQUIREMENTS AND STANDARD COMPLIANCE TEMPLATE FOR REGISTERED MINI-GRIDS

(Applicable to Registered Mini-Grids up to 100 kW of Distributed Power)

2. General Principles

2.1 A registered mini-grid shall be designed and operated to protect life and property, customer equipment, and the integrity of the mini-grid system.

2.2 The operator shall enable the safe use of standard domestic appliances, except where high-power appliances are expressly restricted and suitable overcurrent protection is provided.

2.3 The operator may adopt standards more stringent than those stated in this Schedule, but no registered mini-grid should be designed below the minimum recommendations set out herein.

2.4 The operator shall keep adequate technical records, drawings, equipment schedules, and commissioning evidence sufficient to demonstrate conformity with this Schedule.

3. Standard Technical Requirement Matrix

| Requirement Area | Minimum Requirement / Recommendation | Compliance Recording |
| --- | --- | --- |
| Customer supply voltage | 50 Hz alternating current supply; nominally 230 V between phase and neutral or 400 V between phases. During normal operation, voltage at the customer transfer point should not exceed +10% of nominal value and should not fall below -14% at the most distant socket. DC-supply to customers is not permitted. | Record actual system voltage, frequency, and design basis. |
| Distribution voltage class | Only low-voltage distribution shall be used for registered mini-grids. | Record network voltage level and confirm low-voltage-only distribution. |
| Pole integrity | Poles shall be suitable for actual load and should not tilt or deflect more than 5° from vertical position. | Record pole type, spacing, and structural condition. |
| Main conductor size | Aluminium conductor cross-section should not be less than 16 mm² up to the customer connection point. Larger cross-sections shall be used where required by load and distance. | Record conductor material, cross-section, and design current. |
| Voltage-drop and fault-clearing design | The network shall be dimensioned so that voltage limits are met at maximum continuous load and customer overcurrent protection can trip within fractions of a second under fault conditions. | Record load-flow / voltage-drop basis and fault-clearing assumption. |
| Network arrangement | A simple radial distribution arrangement is recommended | Record network topology. |
| Clearances and insulation | Where safety distance of 1 m from persons, buildings, and vehicles cannot always be guaranteed, active conductors shall be insulated for 600 V. Conductors below 4 m clearance shall be insulated. | Record conductor type, insulation type, and clearance category. |
| Minimum clearance heights | Minimum overhead clearances: 6.5 m over trunk roads; 4 m over side roads; 3 m over closely adjacent buildings, footpaths, and cycle paths. | Record route category and actual clearance. |
| Building-to-building service exception | A neighbouring building may be connected from another building only by an insulated line not exceeding 15 m between attachment points, with total cable length to nearest pole not exceeding 100 m and minimum height of 3 m maintained. | Record any exception used and verify limits. |
| Earthing at source | Neutral conductor at source shall be earthed. | Record earthing arrangement and test results. |
| Residual-current protection | In TT systems, each end customer shall have earth-leakage protection. In TN-C-S systems, omission of residual-current protection is acceptable only where multiple earthing is sufficiently low-impedance. | Record network earthing system and customer protection arrangement. |
| Metering or power limiting | An energy meter or power limiter shall be installed at or upstream of the delivery point for each customer. | Record device type and installation point. |
| Customer main switch | A customer-operated main switch shall be installed in each building and shall also serve as current-limiting circuit breaker. | Record switch/circuit-breaker type and rating. |
| Residual-current device at customer premises | Where low earth-resistance of the network neutral cannot be guaranteed throughout the year, an additional residual-current circuit breaker shall be installed in each building. Rated residual current shall not exceed 30 mA and shall at least be Type A. | Record RCBO/RCD type and rating. |
| Recommended end-customer RCBO | A combined RCBO is recommended for each end customer. A 6 A rating (about 1,000 W) is the normal reference level and should be exceeded only exceptionally. | Record actual customer breaker rating. |
| Indoor wiring minimum copper size | Minimum copper conductor cross-section is 1.5 mm² for active and protective conductors where nominal current does not exceed 16 A and total length from transfer point does not exceed 25 m. | Record conductor size and route length. |
| Reduced conductor exception | A fixed 3-core cable may be reduced to 0.75 mm² only where current is limited to 6 A and cable length from transfer point does not exceed 15 m. | Record any exception used and verify criteria. |
| Indoor voltage-drop limit | Voltage drop from the transfer point should not exceed 3% for customer-side wiring and shall be validated by design calculation for higher currents or longer routes. | Record calculation basis. |
| Lighting provision | Each end customer should be able to have permanently installed, switchable lighting for essential interior spaces. | Record lighting points provided. |
| Protection against contact and water | Active conductors shall not be touchable by customers. Equipment exposed to rain, spray, or dripping water shall be suitably protected. Outdoor equipment shall always be treated as exposed. | Record enclosure/IP protection and installation environment. |
| Socket and cable fastening | Sockets should withstand a 5 kg pulling force on the plug. Exposed cables shall be installed in ducts, pipes, or flush-mounted, or otherwise firmly fixed at intervals not exceeding 30 cm. | Record mounting method. |
| Socket accessibility and lighting height | Sockets should not be readily accessible to small children and light fittings should be installed at safe height. | Record installation standard applied. |
| Fault-testing at farthest point | Overcurrent protection in each building should be verified by fault simulation or equivalent test at the most distant socket, demonstrating rapid tripping without significant interruption to the rest of the mini-grid. | Record test method and result. |
| Generation adequacy | Generation and storage should be sized to provide 24-hour supply. | Record design autonomy assumptions and service profile. |
| Generation and storage safety | The operator may choose and combine energy sources and storage, but shall protect generation facilities against unauthorised access and comply with manufacturer specifications and technical standards. | Record technology type, enclosure/access controls, and safety basis. |

4. Standard Compliance Template for Registered Mini-Grids

4.1 Every registration filing or post-commissioning technical record for a registered mini-grid should be supported by the following minimum compliance template.

| Item | Required Entry | Operator Entry / Confirmation |
| --- | --- | --- |
| Project identification | Project name, location, State, LGA, community, operator name |  |
| Installed generation capacity | Total installed distributed generation capacity (kW) |  |
| Technology type | Solar PV / Solar PV + battery / diesel / hybrid / other |  |
| System voltage and frequency | Nominal voltage and frequency supplied to customers |  |
| Distribution arrangement | Radial / other |  |
| Pole and line construction | Pole type, conductor type, conductor size, route length |  |
| Earthing arrangement | TT / TN-C-S / other, with source earthing details |  |
| Customer protection arrangement | MCB / RCBO / RCD details at customer premises |  |
| Metering arrangement | Energy meter / power limiter / prepayment meter / other |  |
| Customer-side wiring standard | Conductor size, route length, voltage-drop check |  |
| Minimum clearance compliance | Roads / footpaths / buildings / special crossings |  |
| Generation and storage protection | Protection against unauthorised access, enclosure/fire/ventilation arrangements where applicable |  |
| Commissioning tests completed | Voltage check / polarity / continuity / earthing / breaker trip / socket fault test / meter verification |  |
| Service profile disclosed to customers | Normal supply hours and any appliance restrictions |  |
| Operator declaration | Confirm compliance with Schedule 7 minimum recommendations |  |

5. Customer Supply and Distribution Requirements

5.1 Customers shall be supplied only with 50 Hz alternating current at standard domestic voltage levels compatible with commercially available appliances.

5.2 The operator shall not supply non-standard AC voltages or DC voltages directly to customers under a registered mini-grid arrangement.

5.3 The distribution system shall be designed so that voltage at the most distant socket remains within the limits stated in paragraph 3 of this Schedule under normal operation.

5.4 The distribution system should use a simple and robust radial layout, with clear conductor routing, adequate conductor sizing, and overhead clearances consistent with this Schedule.

5.5 Where overhead conductors are accessible or insufficiently separated from persons, buildings, or vehicles, insulation shall be provided as stated in paragraph 3 of this Schedule.

6. Customer Installation and Protection Requirements

6.1 Each customer connection shall have a metering or power-limiting device, a customer-accessible main switch, and suitable overcurrent protection.

6.2 Where the neutral earthing conditions of the network do not ensure safe residual-current protection throughout the year, each customer building shall have residual-current protection with rated residual current not exceeding 30 mA.

6.3 The operator shall ensure that sockets, lights, cables, and exposed conductive parts are installed in a manner that reduces risk of contact, mechanical damage, and water ingress.

6.4 The operator shall verify protective device performance by testing or equivalent safe commissioning procedure at the most distant point of utilisation.

7. Generation, Storage, and Site Safety Requirements

7.1 Generation and storage facilities shall be appropriately sized for the declared service profile and shall be installed and operated in accordance with manufacturer specifications and sound engineering practice.

7.2 All generation and storage equipment shall be protected against unauthorised access and located or enclosed so as to reduce the risk of accidental contact, fire, electrocution, or equipment damage.

7.3 Where battery storage is used, the operator shall provide suitable housing, ventilation, isolation, and protection measures proportionate to the battery type and installation environment.

8. Commissioning and Inspection Record

| Commissioning Check | Minimum Expectation | Completed (Yes/No) | Remarks |
| --- | --- | --- | --- |
| Voltage and frequency check | Supply confirmed at nominal values and acceptable tolerance |  |  |
| Polarity / phase identification | Correct customer-side wiring and phase identification |  |  |
| Earthing verification | Source earthing and customer protection earthing verified |  |  |
| Breaker / RCBO operation | Customer protection devices verified |  |  |
| Fault-clearing test | Rapid operation confirmed at farthest point or equivalent verified method |  |  |
| Meter / power limiter verification | Metering or limiting device installed and functioning |  |  |
| Clearance verification | Minimum clearances confirmed on all routes |  |  |
| Physical safety check | Poles, supports, cables, sockets, switches, and enclosures physically secure |  |  |
| Generation-site safety check | Access control, signage, and equipment safety measures verified |  |  |
| Customer disclosure | Service profile and appliance restrictions communicated to customer |  |  |

9. Operator Declaration

I/We hereby declare that the registered mini-grid identified in this Schedule has been designed, installed, commissioned, and is being operated in substantial conformity with the minimum technical recommendations prescribed in Schedule 7 to the Mini-Grid Regulations, 2026, and that adequate records are retained to support this declaration.

Name of registered mini-grid operator: ______________________________

Name and designation of responsible technical representative: ______________________________

Signature: ______________________________

Date: ______________________________

10. Record Retention

10.1 The registered mini-grid operator shall keep, at a minimum, the following records for each site: a basic single-line diagram or wiring layout, equipment list, conductor sizes, earthing arrangement, customer protection arrangement, meter or limiter record, commissioning checklist, and customer service profile.

10.2 The Commission may require production of these records for inspection, post-commissioning review, incident investigation, or compliance verification.